## Final Uncertainty
| Selected Option | Max Irradiance | Expanded uncertainty | uncertainty %
0 | Inst#1 | 992.8428 W/m^2 | 55.5451 | 5.5945

## Exp & Std Uncert
| Component | Expanded uncertainty | Standard uncertainty
0 | calibration | 2.06 | 1.1893
1 | Zenith response | 2 | 1.1547
2 | Azimuth response | 1 | 0.57735
3 | Spectral response | 1 | 0.57735
4 | Tilt response | 0 | 0
5 | Nonlinearty | 0.2 | 0.11547
6 | Temperature response | 0.5 | 0.28868
7 | Aging per year | 0.5 | 0.28868
8 | maintenance | 0 | 0
9 | Directional Error | 0 | 0
10 | Data Logger Accuracy and Setup (CR3000) | 3.695 | 2.1333

## Selected components
| Component | variable | uncertaintyType | distribution | symmetry | incAnalysis | newName
0 | calibration | S | Relative | Rectangular | Symmetric | Yes | SUS_calibration_S_
1 | Zenith response | S | Relative | Rectangular | Symmetric | Yes | SUS_Zenith response_S_
2 | Azimuth response | S | Relative | Rectangular | Symmetric | Yes | SUS_Azimuth response_S_
3 | Spectral response | S | Relative | Rectangular | Symmetric | Yes | SUS_Spectral response_S_
4 | Tilt response | S | Relative | Rectangular | Symmetric | Yes | SUS_Tilt response_S_
5 | Nonlinearty | S | Relative | Rectangular | Symmetric | Yes | SUS_Nonlinearty_S_
6 | Temperature response | S | Relative | Rectangular | Symmetric | Yes | SUS_Temperature response_S_
7 | Aging per year | S | Relative | Rectangular | Symmetric | Yes | SUS_Aging per year_S_
8 | maintenance | S | Relative | Rectangular | Symmetric | Yes | SUS_maintenance_S_
9 | Directional Error | S | Relative | Rectangular | Symmetric | Yes | SUS_Directional Error_S_
10 | Data Logger Accuracy and Setup (CR3000) | S | Relative | Rectangular | Symmetric | Yes | SUS_Data Logger Accuracy and Setup (CR3000)_S_

## Final Calculation
| DATE | Unnamed: 1 | Zenith Angle | Inst#1 | Voltage [uv] | Uv [uV] | Senitivity Coefficient Cv [1/uv/w/m^2] | Senitivity Coefficient Cs [(Wm^-2)^2 uV^-1] | SUS_calibration_S_ | SUS_Zenith response_S_ | SUS_Azimuth response_S_ | SUS_Spectral response_S_ | SUS_Tilt response_S_ | SUS_Nonlinearty_S_ | SUS_Temperature response_S_ | SUS_Aging per year_S_ | SUS_maintenance_S_ | SUS_Directional Error_S_ | SUS_Data Logger Accuracy and Setup (CR3000)_S_ | SUS_relative_V | SUS_relative_S | SUS_relative_E | Combined Uncertainty Wm^-2 | Combined Uncertainty % | ExpUncert Wm^-2 | ExpUncert % of Reading | UPCAL_calibration_S_ | UPCAL_Zenith response_S_ | UPCAL_Azimuth response_S_ | UPCAL_Spectral response_S_ | UPCAL_Tilt response_S_ | UPCAL_Nonlinearty_S_ | UPCAL_Temperature response_S_ | UPCAL_Aging per year_S_ | UPCAL_maintenance_S_ | UPCAL_Directional Error_S_ | Sum of Stand Uncert * Data Logger | Cont %_calibration_S_ | Cont %_Zenith response_S_ | Cont %_Azimuth response_S_ | Cont %_Spectral response_S_ | Cont %_Tilt response_S_ | Cont %_Nonlinearty_S_ | Cont %_Temperature response_S_ | Cont %_Aging per year_S_ | Cont %_maintenance_S_ | Cont %_Directional Error_S_ | Total %
0 | 4/1/2011 | 07:00:00 | 80.7065 | 138.5691 | 1508.3247 | 2.4816 | 0.09187 | 12.7303 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.4816 | 0.31066 | 0 | 3.9614 | 2.8588 | 7.7643 | 5.6032 | 1.6481 | 1.6001 | 0.80003 | 0.80003 | 0 | 0.16001 | 0.40001 | 0.40001 | 0 | 0 | 5.8082 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
1 | 4/1/2011 | 08:00:00 | 70.661 | 326.8912 | 3558.2107 | 2.955 | 0.09187 | 30.0313 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.955 | 0.31066 | 0 | 9.3336 | 2.8552 | 18.2938 | 5.5963 | 3.8879 | 3.7746 | 1.8873 | 1.8873 | 0 | 0.37746 | 0.94365 | 0.94365 | 0 | 0 | 13.7019 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
2 | 4/1/2011 | 09:00:00 | 59.5833 | 535.7395 | 5831.5245 | 3.48 | 0.09187 | 49.2181 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 3.48 | 0.31066 | 0 | 15.2936 | 2.8547 | 29.9754 | 5.5951 | 6.3718 | 6.1862 | 3.0931 | 3.0931 | 0 | 0.61862 | 1.5465 | 1.5465 | 0 | 0 | 22.4559 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
3 | 4/1/2011 | 10:00:00 | 49.4628 | 575.6633 | 6266.095 | 3.5804 | 0.09187 | 52.8859 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 3.5804 | 0.31066 | 0 | 16.433 | 2.8546 | 32.2086 | 5.595 | 6.8466 | 6.6472 | 3.3236 | 3.3236 | 0 | 0.66472 | 1.6618 | 1.6618 | 0 | 0 | 24.1293 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
4 | 4/1/2011 | 11:00:00 | 41.1822 | 414.8613 | 4515.7653 | 3.1762 | 0.09187 | 38.1131 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 3.1762 | 0.31066 | 0 | 11.8439 | 2.8549 | 23.214 | 5.5956 | 4.9341 | 4.7904 | 2.3952 | 2.3952 | 0 | 0.47904 | 1.1976 | 1.1976 | 0 | 0 | 17.3892 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
5 | 4/1/2011 | 12:00:00 | 36.1498 | 519.7438 | 5657.4113 | 3.4398 | 0.09187 | 47.7486 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 3.4398 | 0.31066 | 0 | 14.8371 | 2.8547 | 29.0806 | 5.5952 | 6.1815 | 6.0015 | 3.0007 | 3.0007 | 0 | 0.60015 | 1.5004 | 1.5004 | 0 | 0 | 21.7854 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
6 | 4/1/2011 | 13:00:00 | 35.791 | 787.2123 | 8568.8059 | 4.1122 | 0.09187 | 72.3208 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 4.1122 | 0.31066 | 0 | 22.4705 | 2.8544 | 44.0422 | 5.5947 | 9.3626 | 9.0899 | 4.545 | 4.545 | 0 | 0.90899 | 2.2725 | 2.2725 | 0 | 0 | 32.9965 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
7 | 4/1/2011 | 14:00:00 | 40.2267 | 834.755 | 9086.3082 | 4.2317 | 0.09187 | 76.6886 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 4.2317 | 0.31066 | 0 | 23.8274 | 2.8544 | 46.7017 | 5.5947 | 9.9281 | 9.6389 | 4.8195 | 4.8195 | 0 | 0.96389 | 2.4097 | 2.4097 | 0 | 0 | 34.9893 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
8 | 4/1/2011 | 15:00:00 | 48.1385 | 695.1545 | 7566.7567 | 3.8808 | 0.09187 | 63.8635 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 3.8808 | 0.31066 | 0 | 19.8432 | 2.8545 | 38.8926 | 5.5948 | 8.2678 | 8.027 | 4.0135 | 4.0135 | 0 | 0.8027 | 2.0067 | 2.0067 | 0 | 0 | 29.1378 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
9 | 4/1/2011 | 16:00:00 | 58.0547 | 578.6102 | 6298.172 | 3.5878 | 0.09187 | 53.1567 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 3.5878 | 0.31066 | 0 | 16.5171 | 2.8546 | 32.3734 | 5.595 | 6.8817 | 6.6812 | 3.3406 | 3.3406 | 0 | 0.66812 | 1.6703 | 1.6703 | 0 | 0 | 24.2528 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
10 | 4/1/2011 | 17:00:00 | 69.0008 | 141.6507 | 1541.8679 | 2.4894 | 0.09187 | 13.0134 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.4894 | 0.31066 | 0 | 4.0492 | 2.8586 | 7.9365 | 5.6029 | 1.6847 | 1.6356 | 0.81782 | 0.81782 | 0 | 0.16356 | 0.40891 | 0.40891 | 0 | 0 | 5.9374 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
11 | 4/1/2011 | 18:00:00 | 79.7985 | 79.9389 | 870.1349 | 2.3343 | 0.09187 | 7.344 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.3343 | 0.31066 | 0 | 2.2915 | 2.8666 | 4.4914 | 5.6186 | 0.95075 | 0.92305 | 0.46153 | 0.46153 | 0 | 0.092305 | 0.23076 | 0.23076 | 0 | 0 | 3.3507 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
12 | 4/2/2011 | 07:00:00 | 80.5015 | 66.264 | 721.2836 | 2.2999 | 0.09187 | 6.0876 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.2999 | 0.31066 | 0 | 1.903 | 2.8718 | 3.7298 | 5.6287 | 0.78811 | 0.76515 | 0.38258 | 0.38258 | 0 | 0.076515 | 0.19129 | 0.19129 | 0 | 0 | 2.7775 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
13 | 4/2/2011 | 08:00:00 | 70.3267 | 219.9353 | 2393.9957 | 2.6862 | 0.09187 | 20.2054 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.6862 | 0.31066 | 0 | 6.2819 | 2.8562 | 12.3125 | 5.5982 | 2.6158 | 2.5396 | 1.2698 | 1.2698 | 0 | 0.25396 | 0.6349 | 0.6349 | 0 | 0 | 9.2187 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
14 | 4/2/2011 | 09:00:00 | 59.1812 | 482.8859 | 5256.213 | 3.3472 | 0.09187 | 44.3625 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 3.3472 | 0.31066 | 0 | 13.7852 | 2.8547 | 27.019 | 5.5953 | 5.7432 | 5.5759 | 2.7879 | 2.7879 | 0 | 0.55759 | 1.394 | 1.394 | 0 | 0 | 20.2405 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
15 | 4/2/2011 | 10:00:00 | 49.1182 | 718.844 | 7824.6169 | 3.9403 | 0.09187 | 66.0399 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 3.9403 | 0.31066 | 0 | 20.5193 | 2.8545 | 40.2178 | 5.5948 | 8.5495 | 8.3005 | 4.1502 | 4.1502 | 0 | 0.83005 | 2.0751 | 2.0751 | 0 | 0 | 30.1308 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
16 | 4/2/2011 | 11:00:00 | 40.808 | 801.208 | 8721.1491 | 4.1474 | 0.09187 | 73.6066 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 4.1474 | 0.31066 | 0 | 22.87 | 2.8544 | 44.8251 | 5.5947 | 9.5291 | 9.2516 | 4.6258 | 4.6258 | 0 | 0.92516 | 2.3129 | 2.3129 | 0 | 0 | 33.5831 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
17 | 4/2/2011 | 12:00:00 | 35.7598 | 906.8293 | 9870.8369 | 4.4129 | 0.09187 | 83.31 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 4.4129 | 0.31066 | 0 | 25.8844 | 2.8544 | 50.7335 | 5.5946 | 10.7853 | 10.4712 | 5.2356 | 5.2356 | 0 | 1.0471 | 2.6178 | 2.6178 | 0 | 0 | 38.0103 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
18 | 4/2/2011 | 13:00:00 | 35.4218 | 972.2527 | 10582.9706 | 4.5773 | 0.09187 | 89.3204 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 4.5773 | 0.31066 | 0 | 27.7517 | 2.8544 | 54.3933 | 5.5946 | 11.5634 | 11.2266 | 5.6133 | 5.6133 | 0 | 1.1227 | 2.8067 | 2.8067 | 0 | 0 | 40.7526 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
19 | 4/2/2011 | 14:00:00 | 39.9125 | 535.52 | 5829.1352 | 3.4795 | 0.09187 | 49.198 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 3.4795 | 0.31066 | 0 | 15.2873 | 2.8547 | 29.9631 | 5.5951 | 6.3692 | 6.1837 | 3.0918 | 3.0918 | 0 | 0.61837 | 1.5459 | 1.5459 | 0 | 0 | 22.4467 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
20 | 4/2/2011 | 15:00:00 | 47.8793 | 761.3687 | 8287.4983 | 4.0472 | 0.09187 | 69.9466 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 4.0472 | 0.31066 | 0 | 21.7329 | 2.8545 | 42.5966 | 5.5947 | 9.0553 | 8.7915 | 4.3958 | 4.3958 | 0 | 0.87915 | 2.1979 | 2.1979 | 0 | 0 | 31.9132 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
21 | 4/2/2011 | 16:00:00 | 57.8362 | 595.462 | 6481.6039 | 3.6302 | 0.09187 | 54.7048 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 3.6302 | 0.31066 | 0 | 16.998 | 2.8546 | 33.3161 | 5.595 | 7.0821 | 6.8758 | 3.4379 | 3.4379 | 0 | 0.68758 | 1.719 | 1.719 | 0 | 0 | 24.9592 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
22 | 4/2/2011 | 17:00:00 | 68.8042 | 386.9842 | 4212.323 | 3.1061 | 0.09187 | 35.5521 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 3.1061 | 0.31066 | 0 | 11.0484 | 2.855 | 21.6548 | 5.5958 | 4.6026 | 4.4685 | 2.2343 | 2.2343 | 0 | 0.44685 | 1.1171 | 1.1171 | 0 | 0 | 16.2207 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
23 | 4/2/2011 | 18:00:00 | 79.7067 | 160.9636 | 1752.0888 | 2.5379 | 0.09187 | 14.7877 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.5379 | 0.31066 | 0 | 4.5999 | 2.8577 | 9.0158 | 5.6011 | 1.9144 | 1.8586 | 0.92932 | 0.92932 | 0 | 0.18586 | 0.46466 | 0.46466 | 0 | 0 | 6.7469 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
24 | 4/3/2011 | 07:00:00 | 80.3943 | 143.6767 | 1563.9209 | 2.4945 | 0.09187 | 13.1995 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.4945 | 0.31066 | 0 | 4.107 | 2.8585 | 8.0497 | 5.6026 | 1.7088 | 1.659 | 0.82952 | 0.82952 | 0 | 0.1659 | 0.41476 | 0.41476 | 0 | 0 | 6.0223 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
25 | 4/3/2011 | 08:00:00 | 70.0222 | 402.5587 | 4381.8514 | 3.1453 | 0.09187 | 36.9829 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 3.1453 | 0.31066 | 0 | 11.4928 | 2.8549 | 22.5259 | 5.5957 | 4.7878 | 4.6483 | 2.3242 | 2.3242 | 0 | 0.46483 | 1.1621 | 1.1621 | 0 | 0 | 16.8735 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
26 | 4/3/2011 | 09:00:00 | 58.9437 | 283.6367 | 3087.3855 | 2.8463 | 0.09187 | 26.0576 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.8463 | 0.31066 | 0 | 8.0993 | 2.8555 | 15.8747 | 5.5968 | 3.3734 | 3.2752 | 1.6376 | 1.6376 | 0 | 0.32752 | 0.81879 | 0.81879 | 0 | 0 | 11.8888 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
27 | 4/3/2011 | 10:00:00 | 48.775 | 379.253 | 4128.1689 | 3.0867 | 0.09187 | 34.8418 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 3.0867 | 0.31066 | 0 | 10.8277 | 2.855 | 21.2224 | 5.5958 | 4.5106 | 4.3792 | 2.1896 | 2.1896 | 0 | 0.43792 | 1.0948 | 1.0948 | 0 | 0 | 15.8966 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
28 | 4/3/2011 | 11:00:00 | 41.4794 | 145.62 | 1585.0737 | 2.4994 | 0.09187 | 13.378 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.4994 | 0.31066 | 0 | 4.1624 | 2.8584 | 8.1583 | 5.6024 | 1.7319 | 1.6815 | 0.84074 | 0.84074 | 0 | 0.16815 | 0.42037 | 0.42037 | 0 | 0 | 6.1038 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
29 | 4/3/2011 | 12:00:00 | 34.791 | 70.06 | 762.6031 | 2.3094 | 0.09187 | 6.4364 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.3094 | 0.31066 | 0 | 2.0108 | 2.8701 | 3.9411 | 5.6253 | 0.83325 | 0.80898 | 0.40449 | 0.40449 | 0 | 0.080898 | 0.20225 | 0.20225 | 0 | 0 | 2.9366 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
30 | 4/3/2011 | 13:00:00 | 35.3483 | 122.2179 | 1330.3418 | 2.4405 | 0.09187 | 11.2281 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.4405 | 0.31066 | 0 | 3.4953 | 2.8599 | 6.8509 | 5.6055 | 1.4536 | 1.4113 | 0.70563 | 0.70563 | 0 | 0.14113 | 0.35281 | 0.35281 | 0 | 0 | 5.1228 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
31 | 4/3/2011 | 14:00:00 | 38.65 | 154.2703 | 1679.2322 | 2.5211 | 0.09187 | 14.1727 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.5211 | 0.31066 | 0 | 4.409 | 2.858 | 8.6417 | 5.6017 | 1.8348 | 1.7814 | 0.89068 | 0.89068 | 0 | 0.17814 | 0.44534 | 0.44534 | 0 | 0 | 6.4663 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
32 | 4/3/2011 | 15:00:00 | 47.5603 | 135.3302 | 1473.0692 | 2.4735 | 0.09187 | 12.4327 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.4735 | 0.31066 | 0 | 3.8691 | 2.859 | 7.5834 | 5.6036 | 1.6095 | 1.5627 | 0.78133 | 0.78133 | 0 | 0.15627 | 0.39066 | 0.39066 | 0 | 0 | 5.6725 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
33 | 4/3/2011 | 16:00:00 | 57.619 | 64.2345 | 699.1925 | 2.2948 | 0.09187 | 5.9012 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.2948 | 0.31066 | 0 | 1.8454 | 2.8728 | 3.6169 | 5.6308 | 0.76397 | 0.74172 | 0.37086 | 0.37086 | 0 | 0.074172 | 0.18543 | 0.18543 | 0 | 0 | 2.6924 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
34 | 4/3/2011 | 17:00:00 | 67.3407 | 43.7934 | 476.6912 | 2.2434 | 0.09187 | 4.0233 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.2434 | 0.31066 | 0 | 1.2668 | 2.8926 | 2.4828 | 5.6695 | 0.52085 | 0.50568 | 0.25284 | 0.25284 | 0 | 0.050568 | 0.12642 | 0.12642 | 0 | 0 | 1.8356 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
35 | 4/3/2011 | 18:00:00 | 78.9607 | 18.9093 | 205.8277 | 2.1808 | 0.09187 | 1.7372 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.1808 | 0.31066 | 0 | 0.57567 | 3.0444 | 1.1283 | 5.967 | 0.2249 | 0.21835 | 0.10917 | 0.10917 | 0 | 0.021835 | 0.054586 | 0.054586 | 0 | 0 | 0.7926 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
36 | 4/4/2011 | 07:00:00 | 80.193 | 160.1656 | 1743.4026 | 2.5359 | 0.09187 | 14.7143 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.5359 | 0.31066 | 0 | 4.5771 | 2.8577 | 8.9712 | 5.6012 | 1.9049 | 1.8494 | 0.92472 | 0.92472 | 0 | 0.18494 | 0.46236 | 0.46236 | 0 | 0 | 6.7134 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
37 | 4/4/2011 | 08:00:00 | 69.7198 | 367.396 | 3999.1055 | 3.0569 | 0.09187 | 33.7525 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 3.0569 | 0.31066 | 0 | 10.4894 | 2.8551 | 20.5592 | 5.5959 | 4.3696 | 4.2423 | 2.1212 | 2.1212 | 0 | 0.42423 | 1.0606 | 1.0606 | 0 | 0 | 15.3996 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
38 | 4/4/2011 | 09:00:00 | 58.5853 | 578.6972 | 6299.119 | 3.588 | 0.09187 | 53.1646 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 3.588 | 0.31066 | 0 | 16.5195 | 2.8546 | 32.3783 | 5.595 | 6.8827 | 6.6822 | 3.3411 | 3.3411 | 0 | 0.66822 | 1.6706 | 1.6706 | 0 | 0 | 24.2565 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
39 | 4/4/2011 | 10:00:00 | 48.434 | 757.8188 | 8248.8576 | 4.0383 | 0.09187 | 69.6205 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 4.0383 | 0.31066 | 0 | 21.6316 | 2.8545 | 42.398 | 5.5947 | 9.0131 | 8.7505 | 4.3753 | 4.3753 | 0 | 0.87505 | 2.1876 | 2.1876 | 0 | 0 | 31.7645 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
40 | 4/4/2011 | 11:00:00 | 40.065 | 884.6518 | 9629.4348 | 4.3571 | 0.09187 | 81.2726 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 4.3571 | 0.31066 | 0 | 25.2515 | 2.8544 | 49.4929 | 5.5946 | 10.5215 | 10.2151 | 5.1075 | 5.1075 | 0 | 1.0215 | 2.5538 | 2.5538 | 0 | 0 | 37.0807 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
41 | 4/4/2011 | 12:00:00 | 34.9845 | 940.0912 | 10232.8927 | 4.4965 | 0.09187 | 86.3658 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 4.4965 | 0.31066 | 0 | 26.8338 | 2.8544 | 52.5942 | 5.5946 | 11.1809 | 10.8552 | 5.4276 | 5.4276 | 0 | 1.0855 | 2.7138 | 2.7138 | 0 | 0 | 39.4045 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
42 | 4/4/2011 | 13:00:00 | 34.6923 | 949.9398 | 10340.0947 | 4.5213 | 0.09187 | 87.2705 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 4.5213 | 0.31066 | 0 | 27.1148 | 2.8544 | 53.1451 | 5.5946 | 11.298 | 10.969 | 5.4845 | 5.4845 | 0 | 1.0969 | 2.7422 | 2.7422 | 0 | 0 | 39.8173 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
43 | 4/4/2011 | 14:00:00 | 39.292 | 889.0023 | 9676.79 | 4.3681 | 0.09187 | 81.6722 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 4.3681 | 0.31066 | 0 | 25.3757 | 2.8544 | 49.7363 | 5.5946 | 10.5733 | 10.2653 | 5.1327 | 5.1327 | 0 | 1.0265 | 2.5663 | 2.5663 | 0 | 0 | 37.2631 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
44 | 4/4/2011 | 15:00:00 | 47.3687 | 659.4157 | 7177.7399 | 3.7909 | 0.09187 | 60.5802 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 3.7909 | 0.31066 | 0 | 18.8232 | 2.8545 | 36.8935 | 5.5949 | 7.8427 | 7.6143 | 3.8071 | 3.8071 | 0 | 0.76143 | 1.9036 | 1.9036 | 0 | 0 | 27.6398 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
45 | 4/4/2011 | 16:00:00 | 57.4028 | 176.9652 | 1926.2662 | 2.5782 | 0.09187 | 16.2577 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.5782 | 0.31066 | 0 | 5.0562 | 2.8572 | 9.9102 | 5.6001 | 2.1047 | 2.0434 | 1.0217 | 1.0217 | 0 | 0.20434 | 0.51085 | 0.51085 | 0 | 0 | 7.4176 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
46 | 4/4/2011 | 17:00:00 | 68.414 | 228.9842 | 2492.493 | 2.7089 | 0.09187 | 21.0367 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.7089 | 0.31066 | 0 | 6.54 | 2.8561 | 12.8185 | 5.598 | 2.7234 | 2.6441 | 1.322 | 1.322 | 0 | 0.26441 | 0.66102 | 0.66102 | 0 | 0 | 9.598 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
47 | 4/4/2011 | 18:00:00 | 79.5247 | 137.4419 | 1496.0551 | 2.4788 | 0.09187 | 12.6267 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.4788 | 0.31066 | 0 | 3.9293 | 2.8588 | 7.7013 | 5.6033 | 1.6347 | 1.587 | 0.79352 | 0.79352 | 0 | 0.1587 | 0.39676 | 0.39676 | 0 | 0 | 5.761 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
48 | 4/5/2011 | 07:00:00 | 80.2319 | 196.0969 | 2134.5148 | 2.6263 | 0.09187 | 18.0153 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.6263 | 0.31066 | 0 | 5.6019 | 2.8567 | 10.9797 | 5.5991 | 2.3323 | 2.2643 | 1.1322 | 1.1322 | 0 | 0.22643 | 0.56608 | 0.56608 | 0 | 0 | 8.2195 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
49 | 4/5/2011 | 08:00:00 | 69.275 | 313.9036 | 3416.8407 | 2.9224 | 0.09187 | 28.8382 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.9224 | 0.31066 | 0 | 8.963 | 2.8553 | 17.5674 | 5.5964 | 3.7334 | 3.6246 | 1.8123 | 1.8123 | 0 | 0.36246 | 0.90616 | 0.90616 | 0 | 0 | 13.1575 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
50 | 4/5/2011 | 09:00:00 | 58.2836 | 504.4163 | 5490.5714 | 3.4013 | 0.09187 | 46.3405 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 3.4013 | 0.31066 | 0 | 14.3996 | 2.8547 | 28.2233 | 5.5952 | 5.9992 | 5.8245 | 2.9122 | 2.9122 | 0 | 0.58245 | 1.4561 | 1.4561 | 0 | 0 | 21.1429 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
51 | 4/5/2011 | 10:00:00 | 48.0968 | 765.124 | 8328.3747 | 4.0567 | 0.09187 | 70.2916 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 4.0567 | 0.31066 | 0 | 21.8401 | 2.8545 | 42.8066 | 5.5947 | 9.0999 | 8.8349 | 4.4174 | 4.4174 | 0 | 0.88349 | 2.2087 | 2.2087 | 0 | 0 | 32.0707 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
52 | 4/5/2011 | 11:00:00 | 39.6972 | 914.9133 | 9958.8313 | 4.4332 | 0.09187 | 84.0527 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 4.4332 | 0.31066 | 0 | 26.1152 | 2.8544 | 51.1857 | 5.5946 | 10.8814 | 10.5645 | 5.2823 | 5.2823 | 0 | 1.0565 | 2.6411 | 2.6411 | 0 | 0 | 38.3492 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
53 | 4/5/2011 | 12:00:00 | 34.6 | 992.8428 | 10807.0939 | 4.6291 | 0.09187 | 91.212 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 4.6291 | 0.31066 | 0 | 28.3393 | 2.8544 | 55.5451 | 5.5945 | 11.8083 | 11.4644 | 5.7322 | 5.7322 | 0 | 1.1464 | 2.8661 | 2.8661 | 0 | 0 | 41.6156 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
54 | 4/5/2011 | 13:00:00 | 34.3073 | 947.6463 | 10315.13 | 4.5155 | 0.09187 | 87.0598 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 4.5155 | 0.31066 | 0 | 27.0494 | 2.8544 | 53.0168 | 5.5946 | 11.2708 | 10.9425 | 5.4712 | 5.4712 | 0 | 1.0942 | 2.7356 | 2.7356 | 0 | 0 | 39.7212 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
55 | 4/5/2011 | 14:00:00 | 39.0248 | 791.1445 | 8611.6079 | 4.1221 | 0.09187 | 72.6821 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 4.1221 | 0.31066 | 0 | 22.5828 | 2.8544 | 44.2622 | 5.5947 | 9.4094 | 9.1353 | 4.5677 | 4.5677 | 0 | 0.91353 | 2.2838 | 2.2838 | 0 | 0 | 33.1613 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
56 | 4/5/2011 | 15:00:00 | 47.1163 | 767.1345 | 8350.259 | 4.0617 | 0.09187 | 70.4763 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 4.0617 | 0.31066 | 0 | 21.8975 | 2.8545 | 42.9191 | 5.5947 | 9.1238 | 8.8581 | 4.4291 | 4.4291 | 0 | 0.88581 | 2.2145 | 2.2145 | 0 | 0 | 32.1549 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
57 | 4/5/2011 | 16:00:00 | 57.189 | 562.227 | 6119.8409 | 3.5466 | 0.09187 | 51.6515 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 3.5466 | 0.31066 | 0 | 16.0495 | 2.8546 | 31.457 | 5.5951 | 6.6868 | 6.492 | 3.246 | 3.246 | 0 | 0.6492 | 1.623 | 1.623 | 0 | 0 | 23.5661 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
58 | 4/5/2011 | 17:00:00 | 68.2208 | 389.995 | 4245.0956 | 3.1137 | 0.09187 | 35.8287 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 3.1137 | 0.31066 | 0 | 11.1343 | 2.855 | 21.8232 | 5.5958 | 4.6384 | 4.5033 | 2.2516 | 2.2516 | 0 | 0.45033 | 1.1258 | 1.1258 | 0 | 0 | 16.3469 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
59 | 4/5/2011 | 18:00:00 | 79.4343 | 167.3516 | 1821.6222 | 2.554 | 0.09187 | 15.3745 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.554 | 0.31066 | 0 | 4.782 | 2.8575 | 9.3728 | 5.6007 | 1.9904 | 1.9324 | 0.9662 | 0.9662 | 0 | 0.19324 | 0.4831 | 0.4831 | 0 | 0 | 7.0146 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
60 | 4/6/2011 | 07:00:00 | 77.1225 | 16.7796 | 182.6459 | 2.1755 | 0.09187 | 1.5415 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.1755 | 0.31066 | 0 | 0.51893 | 3.0926 | 1.0171 | 6.0615 | 0.19957 | 0.19375 | 0.096877 | 0.096877 | 0 | 0.019375 | 0.048439 | 0.048439 | 0 | 0 | 0.70333 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
61 | 4/6/2011 | 08:00:00 | 69.1202 | 35.8797 | 390.5505 | 2.2235 | 0.09187 | 3.2963 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.2235 | 0.31066 | 0 | 1.0442 | 2.9103 | 2.0466 | 5.7041 | 0.42673 | 0.4143 | 0.20715 | 0.20715 | 0 | 0.04143 | 0.10358 | 0.10358 | 0 | 0 | 1.5039 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
62 | 4/6/2011 | 09:00:00 | 57.9998 | 58.7577 | 639.5776 | 2.281 | 0.09187 | 5.398 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.281 | 0.31066 | 0 | 1.69 | 2.8762 | 3.3124 | 5.6374 | 0.69883 | 0.67848 | 0.33924 | 0.33924 | 0 | 0.067848 | 0.16962 | 0.16962 | 0 | 0 | 2.4629 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
63 | 4/6/2011 | 10:00:00 | 47.76 | 127.9297 | 1392.5148 | 2.4549 | 0.09187 | 11.7528 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.4549 | 0.31066 | 0 | 3.6581 | 2.8595 | 7.1699 | 5.6046 | 1.5215 | 1.4772 | 0.7386 | 0.7386 | 0 | 0.14772 | 0.3693 | 0.3693 | 0 | 0 | 5.3623 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
64 | 4/6/2011 | 11:00:00 | 39.3313 | 132.9683 | 1447.3599 | 2.4676 | 0.09187 | 12.2157 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.4676 | 0.31066 | 0 | 3.8017 | 2.8591 | 7.4514 | 5.6039 | 1.5814 | 1.5354 | 0.76769 | 0.76769 | 0 | 0.15354 | 0.38385 | 0.38385 | 0 | 0 | 5.5735 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
65 | 4/6/2011 | 12:00:00 | 34.217 | 225.9232 | 2459.174 | 2.7012 | 0.09187 | 20.7555 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.7012 | 0.31066 | 0 | 6.4527 | 2.8562 | 12.6473 | 5.5981 | 2.687 | 2.6087 | 1.3044 | 1.3044 | 0 | 0.26087 | 0.65218 | 0.65218 | 0 | 0 | 9.4697 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
66 | 4/6/2011 | 13:00:00 | 34.0209 | 248.5602 | 2705.5778 | 2.7581 | 0.09187 | 22.8351 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.7581 | 0.31066 | 0 | 7.0985 | 2.8559 | 13.9131 | 5.5975 | 2.9562 | 2.8701 | 1.4351 | 1.4351 | 0 | 0.28701 | 0.71753 | 0.71753 | 0 | 0 | 10.4186 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
67 | 4/6/2011 | 14:00:00 | 38.6818 | 200.4707 | 2182.1236 | 2.6372 | 0.09187 | 18.4172 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.6372 | 0.31066 | 0 | 5.7266 | 2.8566 | 11.2242 | 5.5989 | 2.3843 | 2.3148 | 1.1574 | 1.1574 | 0 | 0.23148 | 0.57871 | 0.57871 | 0 | 0 | 8.4029 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
68 | 4/6/2011 | 15:00:00 | 46.8667 | 148.1557 | 1612.6748 | 2.5057 | 0.09187 | 13.611 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.5057 | 0.31066 | 0 | 4.2347 | 2.8583 | 8.3 | 5.6022 | 1.7621 | 1.7108 | 0.85538 | 0.85538 | 0 | 0.17108 | 0.42769 | 0.42769 | 0 | 0 | 6.21 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
69 | 4/6/2011 | 16:00:00 | 56.9768 | 87.6605 | 954.1845 | 2.3537 | 0.09187 | 8.0533 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.3537 | 0.31066 | 0 | 2.5112 | 2.8647 | 4.9219 | 5.6148 | 1.0426 | 1.0122 | 0.50611 | 0.50611 | 0 | 0.10122 | 0.25305 | 0.25305 | 0 | 0 | 3.6743 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
70 | 4/6/2011 | 17:00:00 | 68.0297 | 69.7445 | 759.1689 | 2.3086 | 0.09187 | 6.4074 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.3086 | 0.31066 | 0 | 2.0018 | 2.8702 | 3.9235 | 5.6256 | 0.8295 | 0.80534 | 0.40267 | 0.40267 | 0 | 0.080534 | 0.20134 | 0.20134 | 0 | 0 | 2.9234 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
71 | 4/6/2011 | 18:00:00 | 79.3458 | 28.3897 | 309.0219 | 2.2047 | 0.09187 | 2.6081 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.2047 | 0.31066 | 0 | 0.83518 | 2.9419 | 1.637 | 5.766 | 0.33765 | 0.32782 | 0.16391 | 0.16391 | 0 | 0.032782 | 0.081954 | 0.081954 | 0 | 0 | 1.19 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
72 | 4/7/2011 | 07:00:00 | 79.7907 | 124.7327 | 1357.7154 | 2.4469 | 0.09187 | 11.4591 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.4469 | 0.31066 | 0 | 3.567 | 2.8597 | 6.9913 | 5.6051 | 1.4835 | 1.4403 | 0.72014 | 0.72014 | 0 | 0.14403 | 0.36007 | 0.36007 | 0 | 0 | 5.2282 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
73 | 4/7/2011 | 08:00:00 | 68.986 | 268.7118 | 2924.9279 | 2.8088 | 0.09187 | 24.6864 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.8088 | 0.31066 | 0 | 7.6735 | 2.8557 | 15.04 | 5.5971 | 3.1959 | 3.1028 | 1.5514 | 1.5514 | 0 | 0.31028 | 0.7757 | 0.7757 | 0 | 0 | 11.2632 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
74 | 4/7/2011 | 09:00:00 | 57.7668 | 309.7532 | 3371.6636 | 2.912 | 0.09187 | 28.4569 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.912 | 0.31066 | 0 | 8.8445 | 2.8553 | 17.3353 | 5.5965 | 3.684 | 3.5767 | 1.7884 | 1.7884 | 0 | 0.35767 | 0.89418 | 0.89418 | 0 | 0 | 12.9835 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
75 | 4/7/2011 | 10:00:00 | 47.4267 | 688.751 | 7497.0546 | 3.8647 | 0.09187 | 63.2752 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 3.8647 | 0.31066 | 0 | 19.6604 | 2.8545 | 38.5344 | 5.5948 | 8.1916 | 7.953 | 3.9765 | 3.9765 | 0 | 0.7953 | 1.9883 | 1.9883 | 0 | 0 | 28.8694 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
76 | 4/7/2011 | 11:00:00 | 38.9678 | 809.81 | 8814.7818 | 4.169 | 0.09187 | 74.3969 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 4.169 | 0.31066 | 0 | 23.1155 | 2.8544 | 45.3063 | 5.5947 | 9.6314 | 9.3509 | 4.6754 | 4.6754 | 0 | 0.93509 | 2.3377 | 2.3377 | 0 | 0 | 33.9437 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
77 | 4/7/2011 | 12:00:00 | 33.8367 | 897.5993 | 9770.3684 | 4.3897 | 0.09187 | 82.462 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 4.3897 | 0.31066 | 0 | 25.621 | 2.8544 | 50.2172 | 5.5946 | 10.6755 | 10.3646 | 5.1823 | 5.1823 | 0 | 1.0365 | 2.5911 | 2.5911 | 0 | 0 | 37.6234 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
78 | 4/7/2011 | 13:00:00 | 33.6117 | 941.778 | 10251.2535 | 4.5007 | 0.09187 | 86.5207 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 4.5007 | 0.31066 | 0 | 26.8819 | 2.8544 | 52.6885 | 5.5946 | 11.201 | 10.8747 | 5.4374 | 5.4374 | 0 | 1.0875 | 2.7187 | 2.7187 | 0 | 0 | 39.4752 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
79 | 4/7/2011 | 14:00:00 | 38.3787 | 582.2013 | 6337.2612 | 3.5968 | 0.09187 | 53.4866 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 3.5968 | 0.31066 | 0 | 16.6195 | 2.8546 | 32.5743 | 5.595 | 6.9244 | 6.7227 | 3.3613 | 3.3613 | 0 | 0.67227 | 1.6807 | 1.6807 | 0 | 0 | 24.4033 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
80 | 4/7/2011 | 15:00:00 | 47.9976 | 670.9415 | 7303.1982 | 3.8199 | 0.09187 | 61.6391 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 3.8199 | 0.31066 | 0 | 19.1522 | 2.8545 | 37.5382 | 5.5949 | 7.9798 | 7.7474 | 3.8737 | 3.8737 | 0 | 0.77474 | 1.9368 | 1.9368 | 0 | 0 | 28.1229 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
81 | 4/7/2011 | 16:00:00 | 56.7658 | 294.0658 | 3200.9062 | 2.8725 | 0.09187 | 27.0157 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.8725 | 0.31066 | 0 | 8.3969 | 2.8555 | 16.4579 | 5.5967 | 3.4974 | 3.3956 | 1.6978 | 1.6978 | 0 | 0.33956 | 0.84889 | 0.84889 | 0 | 0 | 12.326 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
82 | 4/7/2011 | 17:00:00 | 67.6361 | 162.2153 | 1765.7135 | 2.5411 | 0.09187 | 14.9026 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.5411 | 0.31066 | 0 | 4.6356 | 2.8577 | 9.0857 | 5.601 | 1.9293 | 1.8731 | 0.93655 | 0.93655 | 0 | 0.18731 | 0.46828 | 0.46828 | 0 | 0 | 6.7994 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100
83 | 4/7/2011 | 18:00:00 | 79.2573 | 123.875 | 1348.3794 | 2.4447 | 0.09187 | 11.3803 | 0.01676 | 0.015798 | 0.0039494 | 0.0039494 | 0 | 0.00015798 | 0.00098736 | 0.00098736 | 0 | 0 | 0.053922 | 2.4447 | 0.31066 | 0 | 3.5426 | 2.8598 | 6.9434 | 5.6052 | 1.4733 | 1.4304 | 0.71519 | 0.71519 | 0 | 0.14304 | 0.3576 | 0.3576 | 0 | 0 | 5.1923 | 28.3747 | 27.5482 | 13.7741 | 13.7741 | 0 | 2.7548 | 6.8871 | 6.8871 | 0 | 0 | 100